Arc-Flash Hazard PPE Categories for Alternating Current Systems

| Equipment | Arc Flash PPE Category | Arc-Flash Boundary |
| --- | --- | --- |
| Panelboards or other equipment rated 240V and below Parameters: Maximum of 25 kA short-circuit current available; maximum of 0.03 sec (2 cycles) fault clearing time; working distance 455 mm (18 in.) | 1 | 485 mm (19 in) |
| Panelboards or other equipment rated >240V and up to 600V Parameters: Maximum of 25 kA short-circuit current available; maximum 0.03 sec (2 cycles) fault clearing time; working distance 455 mm (18 in | 2 | 900 mm (3ft) |
| 600-V class motor control centers (MCCs) Parameters: Maximum of 65 kA short-circuit current available; maximum of 0.03 sec (2 cycles) fault clearing time; working distance 455 (18 in.) | 2 | 1.5m (5 ft) |
| 600-V class motor control centers (MCCs) Parameters: Maximum of 42 kA short-circuit current available; maximum of 0.33 sec (20 cycles) fault clearing time; working distance 455 mm (18 in.) | 4 | 4.3 m (14 ft) |
| 600-V class switchgear (with power circuit breakers or fused switches) and 600 V class switchboards Parameters: Maximum of 35 kA short-circuit current available; maximum of up to 0.5 sec (30 cycles) fault clearing time; working distance 455 mm (18 in.) | 4 | 6 m (20 ft) |
| Other 600-V class (277 V through 600 V, nominal) equipment Parameters: Maximum of 65 kA short circuit current available; maximum of 0.03 sec (2 cycles) fault clearing time; working distance 455 mm (18 in.) | 2 | 1.5 m (5 ft) |
| NEMA E2 (fused contactor) motor starters, 2.3 kV through 7.2 kV Parameters: Maximum of 35 kA short-circuit current available; maximum of up to 0.24 sec (15 cycles) fault clearing time; working distance 910 mm (36 in.) | 4 | 12m (40 ft) |
| Metal-clad switchgear, 1 kV through 15 kV Parameters: Maximum of 35 kA sort-circuit current available; maximum of up to 0.24 sec (15 cycles) fault clearing time; working distance 910 mm (36 in.) | 4 | 12m (40 ft) |
| Arc-resistant switchgear Type 1 or 2 [for clearing times of < 0.5 sec (30 cycles) with a perspective fault current not to exceed the arc-resistant rating of the equipment], and metal-enclosure | N/A (doors closed) | N/A (doors closed) |
|  | 4 (doors open) | 12m (40 ft) |
| Other equipment 1 kV through 15 kV 12m Parameters: Maximum of 35 kA short-circuit current available; maximum of up to 0.24 sec (15 cycles) fault clearing time; working distance 910 mm (36 in.) | 4 | 12m (40 ft) |

Note: for equipment rated 600 volts and below, and protected by upstream current limiting fuses or current limiting circuit breakers sized at 200 amperes or less, the arc flash PPE category can be reduced by one number but not below arc flash PPE category 1.