Arc Flash Hazard Identification for Alternating Current (AC) and Direct Current (DC) Systems

| Task | Equipment Condition (see note) | Arc Flash PPE Required |
| --- | --- | --- |
| Reading a panel meter while operating a meter switch | Any | NO |
| Normal operation of a circuit breaker (CB), switch, contactor, or starter | All of the following: The equipment is properly installed The equipment is properly maintained All equipment doors are closed and secured All equipment covers are in place and secured There is no evidence of impending failure | NO |
|  | One or more of the following: The equipment is not properly installed The equipment is not properly maintained Equipment doors are open or not secured Equipment covers are off or not secured There is evidence of impending failure | YES |
| For ac systems: Work on energized electrical conductors and circuit parts, including voltage testing | Any | YES |
| For DC systems: Work on energized electrical Conductors and circuit parts of series-connected battery cells, including voltage testing | Any | YES |
| Voltage testing on individual battery cells or individual multi-cell units | All of the following: The equipment is properly installed The equipment is properly maintained All equipment covers are in place and secured There is no evidence of impending failure | NO |
|  | One or more of the following: The equipment is not properly installed The equipment is not properly maintained Equipment doors are open or not secured Equipment covers are off or not secured There is evidence of impending failure | YES |
| Removal or installation of CBs or switches | Any | YES |
| Removal or installation of covers for equipment such as wireways, junction boxes, and cable trays that does not expose bare energized electrical conductors and circuit parts | All of the following: The equipment is properly installed The equipment is properly maintained There is no evidence of impending failure | NO |
|  | Any of the following: The equipment is not properly installed The equipment is not properly maintained There is evidence of impending failure | YES |
| Removal of bolted covers (to exposed bare energized electrical conductors and circuit parts) For DC systems, this includes bolted covers, such as battery terminal covers. | Any | YES |

| Task | Equipment Condition (see note) | Arc Flash PPE Required |
| --- | --- | --- |
| Removal of battery intercell connector covers | All of the following: The equipment is properly installed The equipment is properly maintained All equipment covers are in place and secured There is no evidence of impending failure | NO |
|  | One or more of the following: The equipment is not properly installed The equipment is not properly maintained Equipment doors are open or not secured Equipment covers are off or not secured There is evidence of impending failure | YES |
| Opening hinged door(s) or cover(s) (to exposed bare energized electrical conductors and circuit parts) | Any | YES |
| Perform infrared thermography and other noncontact inspections outside the restricted approach boundary. This activity does not include opening of hinged doors or covers | Any | NO |
| Application of temporary protective grounding equipment after voltage test. | Any | YES |
| Work on control circuits with exposed energized electrical conductors and circuit parts, 120 volts or below without any other exposed energized equipment over 120 V including opening of hinged covers to gain access | Any | NO |
| Work on control circuits with exposed energized electrical conductors and circuit parts, greater than 120 V | Any | YES |
| Insertion or removal of individual starter buckets from motor control center (MCC) | Any | YES |
| Insertion or removal (racking) of CBs or starters from cubicles, doors open or closed | Any | YES |
| Insertion or removal of plug-in device into or from busways | Any | YES |
| Insulated cable examination with no manipulation of cable | Any | NO |
| Insulated cable examination with manipulation of cable | Any | YES |
| Work on exposed energized electrical conductors and circuit parts of equipment directly supplied by a panelboard or motor control center | Any | YES |
| Insertion or removal of revenue meters (kW-hour, at primary voltage and current) | Any | YES |
| For DC systems, insertion or removal of individual cells or multi-cell units of a battery system in an enclosure | Any | YES |
| For DC systems, insertion or removal of individual cells or multi-cell units of a battery system in an open rack | Any | NO |

| Task | Equipment Condition (see note) | Arc Flash PPE Required |
| --- | --- | --- |
| For DC systems, maintenance on a single cell of a battery system or multi-cell units | Any | NO |
| For DC systems, work on exposed energized electrical conductors and circuit parts of utilization equipment directly supplied by a DC source | Any | YES |
| Arc-resistant switchgear Type 1 or 2 (for clearing times of <0.5 sec with a prospective fault current not to exceed the are-resistant rating of the equipment) and metal enclosed interrupter switchgear, fused or unfused of arc resistant type construction, tested in accordance with IEEE C37.207: - Insertion or removal (racking) of CBs from cubicles - Insertion or removal (racking) of ground and test device - Insertion or removal (racking) of voltage transformers on or off the bus | All of the following: The equipment is properly installed The equipment is properly maintained All equipment doors are closed and secured All equipment covers are in place and secured There is no evidence of impending failure | NO |
|  | One or more of the following: The equipment is not properly installed The equipment is not properly maintained Equipment doors are open or not secured Equipment covers are off or not secured There is evidence of impending failure | YES |
| Open the voltage transformer or control power transformer compartments | Any | YES |
| Outdoor disconnect switch operation (hookstick operated) at 1 kV through 15 kV | Any | YES |
| Outdoor disconnect switch operation (gang-operated, from grade) at 1 kV through 15 kV | Any | YES |

Note: Hazard identification is one component of risk assessment. Risk assessment involves a determination of the likelihood of occurrence of an incident, resulting from a hazard that could cause injury or damage to health. The assessment of the likelihood of occurrence contained in this table does cover every possible condition or situation. Where this table indicates that arc flash PPE is not required, an arc flash is not likely to occur

*The phrase properly installed, as used in this table, means that the equipment is installed in accordance with applicable industry codes and standards and the manufacturer’s recommendations. The phrase properly maintained, as used in this table, means that the equipment has been maintained in accordance with the manufacturer’s recommendations and applicable industry codes and standards. The phrase evidence of impending failure, as used in this table, means that there is evidence or arcing, overheating, loose or bound equipment parts, visible damage, deterioration, or other damage.