Arc-Flash Hazard PPE Categories for Direct Current Systems

| Equipment | Arc Flash PPE Category | Arc-Flash Boundary |
| --- | --- | --- |
| Storage batteries, dc switchboards, and other dc supply sources 100 V > Voltage < 250 V Parameters: Voltage: 250 V Maximum arc duration and working distance: 2 sec @ 455 mm (18 in) |  |  |
| Short-circuit current < 4 kA | 1 | 900 mm (3 ft) |
| 4 kA ≤ short-circuit current < 7 kA | 2 | 1.2 m (4 ft) |
| 7 kA ≤ short-circuit current < 15 kA | 3 | 1.8 m (6 ft) |
| Storage batteries, dc switchboards, and other dc supply sources 250 V > Voltage < 600 V Parameters: Voltage: 600 V Maximum arc duration and working distance: 2 sec @ 455 mm (18 in) |  |  |
| Short-circuit current < 1.5 kA | 1 | 900 mm (3 ft) |
| 1.5 kA ≤ short-circuit current < 3 kA | 2 | 1.2 m (4 ft) |
| 3 kA ≤ short-circuit current < 7 kA | 3 | 1.8 m (6 ft) |
| 7 kA ≤ short-circuit current < 10 kA | 4 | 2.5 m (8 ft) |

Note: Apparel that can be expected to be exposed to electrolyte must meet both of the following conditions:

- Be evaluated for electrolyte protection in accordance with ASTM F1296, standard guide for evaluating chemical protective clothing.

- (2) Be arc-rated in accordance with ASTM F1891, standard specification for arc rated and flame-resistant rainwear, or equivalent.